COB1301	NOx-EMISSIONS CONTROL TECHNIQUES FOR COAL-FUELED POWER PLANTS AND GAS TURBINE-BASED COMBINED CYCLES

Nikolai Khartchenko

Institute for Energy Engineering, Technical University of Berlin.

Marchstr. 18, 10587 Berlin, Germany - E-mail: nik@buran.fb10.tu-berlin.de

Advanced techniques for NOx-emissions control used in coal-fueled power plants and gas turbine-based combined cycles are discussed. The in-furnace NOx control reduces the NOx formation or emissions during combustion by using staged combustion, reburning, flue gas recirculation, low NOx burners (LNBs), and other methods. The NOx emissions reduction in the range of 40 to 60% is achieved with LNBs, 20 to 25% with the burners-out-of-service method, 15 to 25% by using overfire air, up to 15% due to low excess air, and 5% by biased firing. In addition, the paper discusses multi-pollutant emissions control methods. The recently developed processes for simultaneous SO2/NOx removal feature high removal efficiency for the two pollutant species. Thus, in the SNOx-process 96% SO2 and 94% NOx removal is achieved when burning coal with 3.4% sulfur.

Keywords: In-furnace NOx reduction, staged combustion, reburning, multi-pollutant emissions control, low NOx burners.