COB269	ESCOAMENTO TURBULENTO NA SAÍDA DE UM DUTO CURVO DE SEÇÃO RETANGULAR DIVERGENTE - ESTUDO EXPERIMENTAL / TURBULENT FLOW AT OUTLET OF A CURVED RECTANGULAR DIVERGENT DUCT - EXPERIMENTAL STUDY

Maria Luiza Sperb Indrusiak & Sérgio Viçosa Möller

Programa de Pós Graduação em Engenharia Mecânica, Escola de Engenharia - UFRGS - Porto Alegre

CEP 90.050-170 R. Sarmento Leite, 425,Porto Alegre, RS - Brasil - E-mail: svmoller@vortex.ufrgs.br

This paper presents the experimental study of the turbulent flow in a curved duct which simulates part of a thermal-electrical power plant. Ashes, carried in the power plant by the flow of gases from the furnace, impinge on the pipes of the heat exchanger, which pre-heat water prior of the steam generator, after passing a curved duct, and produce erosion of the pipes of the heat exchanger, leading to failures which stop plant operation. Flow distribution after the curve increase the erosion near the concave wall of the duct. Classical solutions for flow redistribution in curves, like vanes, are not applicable since they could increase operational risks due to the erosion of the vanes. This problem was investigated in a scale model of the curved duct, with, for simplicity, air as the working fluid. Flow visualizations with wool threads on the duct wall, Pitot tube and hot wire measurements were applied. Based on the results, modifications in the test section were made, using boundary-layer control techniques. The results show that flow redistribution after the curve was improved, and the modifications, when implemented in the plant, may lead to safer and economical operation conditions.

Keywords: Escoamento turbulento; Dutos retangulares curvos; Anemometria de fio quente; turbulent flow; curved rectangular ducts; hot wire anemometry